## OHE EIG checksheet
| EIG Checklist-OHE |  |  |  | Sheet-1B
Sr. No | Particulars | Proforma no. of ACTM | Attached (Yes/No) | Page no. | Remark
1 | Public notification regarding Energisation (with news paper cutting) | 10.01 | Yes
2 | Introduction of AC 25 kV Traction warning to road users (with news paper cutting) | 10.02
3 | Certificate regarding OHE | 10.03
4 | Certificate regarding Bonding & Earthing | 10.04
5 | Joint Certificate by Divisional officer’s counter signed by DRM regarding safety measures | 10.05
6 | Sanction for Energisation of OHE | 10.07
7 | Details of OHE & PSI Assets for section. |  | No
8 | Certificate by S&T department | 10.08
9 | Clearance certificate by DOT dept. | 10.09
10 | Clearance certificate for 25 kV feeder line | 10.1
11 | Clearance certificate for OHE | 10.11
12 | Clearance certificate for switching stations | 10.12
13 | Clearance certificate for Auxiliary Transformer (OLD ACTM) | 10.13
14 | Clearance certificate by OHE/ AT Contractor | 10.15
15 | Clearance certificate by switching station contractor | 10.16
16 | Clearance certificate by Remote Control equipment contractor | 10.17
17 | Compliance of IE Rules
18 | Compliance of HQ-TC-127 (OHE/PSI) (Sheet attached)
19 | Copy of approved Drawings
(i) | Concept plan showing proposed work in red colour |  | No
(ii) | General supply diagram
(iii) | Sectioining diagram
(iv) | Layout plan (LOP)
(v) | As erected SED
(vi) | TSWR with Appendix-G
20 | Confirmation of provision of T&P items, furniture & other facilities as HQ letter No. EL-92/53 dated: 27.09.2020
21 | RITES Inspection certificates/Consignee Certificate of Equipments at TSS/SWS/AT
22 | Joint checking and certification as per standard format
(i) | SED checking
(ii) | X/O & T/O
(iii) | ATD
(iv) | Isolator
(v) | TW checking
(vi) | Insulator
(vii) | Overlap
(viii) | PTFE
(ix) | Implantation
(x) | Overline structures
(xi) | Overhead crossing
23 | Earth resistance reading.
24 | Testing Equipment List and Calibration certificate
25 | Certificate Regarding Procurement of Material From Approved Sources.
26 | Category wise jointly signed defects/ deficiencies list with PDC
| Dy.CEE/C |  |  |  | Sr.DEE/TRD

## TC-127(OHE)
HQ TC No-127
S.No | Item | Yes/No | Remarks
(i) | Provision of anti falling arrangement for along feeder jumper connected to OHE. | Yes
(ii) | Provision of Cross feeder wire with 150 Copper feeder and Drop jumper of 160 sq mm with Anti falling arrangement of Cross feeder. | Yes
(iii) | Provision of isolators copper jumpers of 160 sq mm with bolt type connector and anti falling arrangement.
(iv) | Provision of Copper feeder wire of 150 sq mm and to run on separate mast.
(v) | Crossings of 150 sq mm copper Feeder wire through gantry arrangement.
(vi) | Privision of "G" jumper with cross type arrangement as per RDSO drawing.
(vii) | Provision of 160 sqmm "G" jumper in Cross over and overlap.
(viii) | Provision of 'G' jumper in overlap zone instead of cross over zone at X/O and T/O locations).
(ix) | Modification of anti falling arrangement of 3-pulley type ATD - RDSO modification vide RDSO letter No.TI/OHE/ATD/10 dated: 31.05.2010 / 04.06.2010.
(x) | Provision of Composite and Porcelain as per latest guidelines issued vide letter No 2002/Elect(G)/161/21 dated: 04.07.12.
(xi) | 100% testing (joint testing) of insulators before providing to the line. (As per the latest guidelines)
(xii) | Provision of standard arrangement of false catenary under overline structure(FOB/ROB) location as per RDSO SMI TI/MI/0062.
(xiii) | Provision of 1600 Amp 25 KV single pole Isolator with 160 sq.mm Copper jumper arrangement- RDSO directives.
(xiv) | Provision of forge fittings instead of MCI fittings as per HQ – TC No.84 & 89.
(xv) | Bonding and earthing of OHE mast for Concrete bridges with provision of Earth wire/strip and earthing on both side of Bridge.
(xvi) | Provision of spare OHE mast foundation on Bridges pier & spare bridge mast as per R.B letter No.2022/EEM/148/4/IRSOD dated: 10.09.2025
(xvii) | Provision of continuous protective screen on FOB and ROB as per the RDSO latest drawing No. ETI/C/0068 Mod-H.
(xviii) | Provision of PTFE Neutral section in place of Insulated over lap of TSS.
(xix) | Standard of OHE design as per ACTM and Cross over/Turn out and overlap layout as per RDSO drawing.
(xx) | Provision of Retro reflective number plates and other caution board on OHE mast as per HQ TC No.59 and R.Bd letter No.2001/Elect(G)/170/1 Pt, dated: 21.02.12
(xxi) | Whether Steady arm with length of 1 meter be provided.
(xxii) | DA implantation at station at Platform should be more than 1.85 meter.
(xxiii) | Whether 4 span overlap available
(xxiv) | Provision of parallel contact wire across RRA clamp.
(xxv) | Provision of Packing Saddle under catenary suspension clamp as per RDSO SMI No. TI/MI/0059 (Rev-2)
(xxvi) | Connection of structure bond to Rail in track circuiting area as per HQ letter No.El-94/15/1(Comp. No. 677982) dated: 17.10.2025
(xxvii) | Any other modification as per Rly.Bd/RDSO/HQ guidelines
| Dy.CEE/C | Sr.DEE/TRD

## Joint checking OHE
Sheet-2
Joint checking of OHE with Contractor/ Construction staff list
S.No | Type of Checking | Unit | Total Qty | Progress | Balance | PDC for Balance | Remarks
1 | SED checking (TKM) | TKM
2 | TW checking (TKM) | TKM
3 | X/O & T/O checking (NOs.) | Nos.
4 | Overlap checking (Nos.) | Nos.
5 | ATD checking (Nos.) | Nos.
6 | Implantation | Nos.
7 | Isolator | Nos.
8 | Overline structures | Nos.
9 | PTFE | Nos.
10 | Insulator | Nos.
11 | Overhead crossing | Nos.
| Dy.CEE/C |  |  |  |  | Sr.DEE/TRD

## PSI EIG Checksheet
| EIG Checklist-PSI (Rayka SSP) |  |  |  | Sheet-1A
Sr. No | Particulars | Proforma no. of ACTM | Attached (Yes/No) | Page no. | Remark
1 | Public notification regarding Energisation | 10.01 | No
2 | Introduction of AC 25 kV Traction warning to road users | 10.02 | Yes
3 | Certificate regarding OHE | 10.03 | Yes
4 | Certificate regarding Bonding & Earthing | 10.04 | Yes
5 | Joint Certificate by Divisional officer’s counter signed by DRM regarding safety measures | 10.05 | Yes
6 | Sanction for Energisation of OHE | 10.07 | Yes
7 | Details of OHE & PSI Assets for section.
8 | Certificate by S&T department | 10.08
9 | Clearance certificate by DOT dept. | 10.09
10 | Clearance certificate for 25 kV feeder line | 10.1 | Yes
11 | Clearance certificate for OHE | 10.11
12 | Clearance certificate for switching stations | 10.12 | Yes
13 | Clearance certificate for Auxiliary Transformer (OLD ACTM) | 10.13
14 | Clearance certificate by OHE/ AT Contractor | 10.15 | Yes
15 | Clearance certificate by switching station contractor | 10.16 | Yes
16 | Clearance certificate by Remote Control equipment contractor | 10.17 | Yes
17 | Compliance of IE Rules
18 | Compliance of HQ-TC-127 (OHE/PSI) |  | Yes
19 | Copy of approved Drawings (for TSS/SWS/AT)
(i) | General supply diagram
(ii) | General arrangement drawing(GAD)
(iii) | Fencing layout plan
(iv) | Foundation layout plan
(v) | Earthing layout plan
(vi) | Cable trench layout plan
(vii) | AT cable route detail drawing
(viii) | AT mast detail drawing.
20 | Confirmation of provision of T&P items, furniture & other facilities as HQ letter No. EL-92/53 dated: 27.09.2020
21 | Index of Testing Equipment List Traction Substation/ SWS
22 | Relay Test Report Traction Substation at as per ACTM/RDSO/I.E. rules guidelines
23 | RITES Inspection certificates/Consignee Certificate of Equipments at TSS/SWS/AT
24 | Layout and Electrical Clearance Details(TSS/SWS)
25 | Pre-commsioning test report for:-
(i) | Traction Transformer
(ii) | Circuit breaker(HV/LV)
(iii) | Interruptor
(iv) | Auxiliary Transformer, DO fuse
(v) | LT cable (for AT)
(vi) | CLS panel
(vii) | CT
(viii) | PT
(ix) | LA
(x) | Battery set
(xi) | Battery Charger
(xii) | DPI, SPI
(xiii) | ACDB, DCDB
(xiv) | Auto Transformer
(xv) | Capacitor bank & reactor
26 | Earth resistance reading (Individual pit & combine)
27 | Testing Equipment List and Calibration certificate
28 | Certificate Regarding Procurement of Material From Approved Sources.
29 | Category wise jointly signed defects/ deficiencies list with PDC
| Dy.CEE/C |  |  |  | Sr.DEE/TRD

## Defects & Deficiensis
Sheet-2
Defects /Deficiencies & pending works list
S.No | Defects/Deficiencies | PDC | Remarks
A | Type A
(i)
(ii)
B | Type B
(i)
(ii)
C | Type C
(i)
(ii)
| Dy.CEE/C |  | Sr.DEE/TRD

## TC-127(PSI)
HQ TC No-127
S.No | Item | Yes/No | Remarks
(i) | Provision of insulating pad and surge monitor to Lightening Arresters – RDSO modification vide RDSO SMI No. TI/SMI/0048 (Rev-2). | Yes
(ii) | Provision of disconnector assembly to Lightening arrestor- RDSO modification vide RDSO SMI No. TI/SMI/0048(Rev-2). | Yes
(iii) | Provision of Earthing station at SP and SSP - RDSO modification vide RDSO SMI No. TI/SMI/0032 (Rev-2). | Yes
(iv) | Provision of Battery monitoring relay at TSS- RDSO modification vide RDSO letter No.TI/PSI/PROCT/STATC/12 dated 01/05.03.2013 & 08/12.03.2013 | No
(v) | Provision of 9-ton insulator with Arcing horn at Auxiliary Transformer - RDSO modification vide RDSO letter No.TI/PSI/AT/POLICY/10 dated 20/31.02.2010. | No
(vi) | Provision of Control and Relay panels as per latest directive of RDSO letter No.TI/PSI/PROCT/STATC/12 dated 01/05.03.2013 & 08/12.03.2013 or latest. | Yes
(vii) | Provision of PT on HT side of Transformer for voltage indication- RDSO modification. | No
(viii) | Provision of ABT Energy meter in TSS with associated CT& PT. | No
(ix) | Provision of PT fuse across PT to isolate PT in case of failure-RDSO modification. | No
(x) | Provision of CB and Protection arrangement for major yard/siding in TSS/SSP for isolation as per RDSO letter No. RDSO-TI0LKO(PSI)/5312020-O/O PED/TI/RDSO dated: 19.03.2024. | Yes
(xi) | Double Earthing arrangement for Lightening Arresters and Auxiliary Transformer with Continuous Earthing patti from LA/AT to Earthing electrodes. | Yes
(xii) | Provision of check energy meter at TSS. | No
(xiii) | Provision of PT on 220/132/110 KV side at TSS. | No
(xiv) | Provision of Duplicate / Stand by cable for Auxiliary Transformers.
(xv) | Provision AT cable route markers
(xvi) | Any other modification as per Rly.Bd/RDSO/HQ guidelines. | No
| Dy.CEE/C | Sr.DEE/TRD